## Sheet1
Label | Value | Notes
Created by checklistguro.com
Pre-Test Inspection (STEP)
Date of Inspection (DATE)
Time of Inspection (DATE)
Generator Model Number (TEXT)
Generator Serial Number (TEXT)
Fuel Level (Gallons/Liters) (NUMBER)
Visual Inspection of Enclosure (SELECTION options: Good, Fair, Poor)
Check for Obvious Damage or Leaks (SELECTION options: Yes, No)
Comments on Pre-Test Conditions (e.g., environmental factors, prior issues) (TEXT)
Start-Up and Run Test (STEP)
Test Start Time (DATE)
Ambient Temperature (°C) (NUMBER)
Generator Voltage (Initial) (NUMBER)
Generator Frequency (Initial) (NUMBER)
Start Attempt Success (First Attempt) (SELECTION options: Yes, No)
Time to Startup (Seconds) (NUMBER)
Generator Load (kW) (NUMBER)
Generator Voltage (During Run) (NUMBER)
Generator Frequency (During Run) (NUMBER)
Observations During Run (TEXT)
Load Bank Testing (If Applicable) (STEP)
Load Bank Voltage (V) (NUMBER)
Load Bank Current (A) (NUMBER)
Generator Voltage (V) at Load (NUMBER)
Generator Frequency (Hz) at Load (NUMBER)
Load Bank Power Output (kW) (NUMBER)
Voltage Dip During Load Application (SELECTION options: Within Specification, Exceeds Specification - Document Details, Voltage Sag Present - Investigate)
Observations during Load Bank Test (TEXT)
Load Acceptance (SELECTION options: Acceptable, Reject - Document Details)
Safety Systems & Monitoring (STEP)
Generator Enclosure Inspection - Secure? (SELECTION options: Yes, No, N/A)
Exhaust System Integrity? (SELECTION options: Yes, No, N/A)
Exhaust Temperature (During Run) (NUMBER)
Low Oil Level Shutdown Function Test (SELECTION options: Passed, Failed, N/A)
High Coolant Temperature Shutdown Function Test (SELECTION options: Passed, Failed, N/A)
Over-Speed Protection Test (SELECTION options: Passed, Failed, N/A)
Notes on Safety System Performance/Observations (TEXT)
Post-Test Inspection (STEP)
Generator Runtime (Hours) (NUMBER)
Cooling System Temperature (Degrees) (NUMBER)
Oil Pressure (PSI) (NUMBER)
Overall Condition (SELECTION options: Excellent, Good, Fair, Poor)
Any Abnormal Noises or Vibrations Observed? (TEXT)
Notes/Comments on Post-Test Condition (TEXT)
Next Scheduled Test Date (DATE)
Inspector Signature (SIGNATURE)
Documentation & Record Keeping (STEP)
Date of Inspection/Test (DATE)
Start Time of Test (DATE)
End Time of Test (DATE)
Generator Run Time (Hours) (NUMBER)
Test Results Summary (TEXT)
Observations/Comments (TEXT)
Load Bank Data/Graphs (if applicable) (UPLOAD)
Overall Status (SELECTION options: Pass, Fail, Conditional Pass)
Next Scheduled Test Date (TEXT)
Inspector Signature (SIGNATURE)