## Sheet1
Label | Value | Notes
Created by checklistguro.com
System Activation & Transfer (STEP)
Time of Emergency Power System Activation (DATE)
Activation Method (SELECTION options: Automatic Transfer, Manual Transfer)
Transfer Time (seconds) (NUMBER)
Transfer Success? (SELECTION options: Yes, No)
Notes on Transfer Process (if any issues) (TEXT)
Synchronization Status (SELECTION options: Synchronized, Not Synchronized)
Voltage Level (Emergency Power) (NUMBER)
Generator Performance (STEP)
Generator Voltage (Volts) (NUMBER)
Generator Frequency (Hz) (NUMBER)
Load Acceptance Time (Seconds) (NUMBER)
Generator Speed (RPM) (NUMBER)
Engine Oil Pressure (PSI) (SELECTION options: Normal, Low, High)
Coolant Temperature (Degrees F) (SELECTION options: Normal, High, Low)
Observations & Anomalies (TEXT)
Time of Load Acceptance (DATE)
Critical Equipment Verification (STEP)
Ventilator Status (SELECTION options: Operational, Not Operational, Partial Functionality)
ECG Monitor Battery Level (%) (NUMBER)
Infusion Pump Status (SELECTION options: Operational, Not Operational, Partial Functionality)
Patient Monitoring System (PMS) Status (SELECTION options: Operational, Not Operational, Partial Functionality)
Oxygen Concentrator Output (LPM) (NUMBER)
Medical Air Pressure (SELECTION options: Within Range, Low, Out of Range)
Any observed abnormalities or issues with critical equipment (TEXT)
Lighting & HVAC (STEP)
Emergency Lighting Status (SELECTION options: Functional, Dim/Weak, Non-Functional)
Emergency Lighting Lumens (average) (NUMBER)
HVAC System Status (SELECTION options: Functional, Partial Functionality, Non-Functional)
Room Temperature (°C) - measured (NUMBER)
Room Temperature (°F) - measured (NUMBER)
HVAC Airflow (observed) (SELECTION options: Adequate, Reduced, Insufficient)
Comments/Observations regarding Lighting and HVAC (TEXT)
Fuel Supply & Monitoring (STEP)
Initial Fuel Level (Gallons/Liters) (NUMBER)
Fuel Consumption During Test (Gallons/Liters) (NUMBER)
Remaining Fuel Level (Gallons/Liters) (NUMBER)
Fuel Type Verified? (SELECTION options: Correct Fuel Type, Incorrect Fuel Type - Investigate)
Fuel Gauge Functionality (SELECTION options: Operational, Malfunctioning - Investigate)
Last Fuel Delivery Date (DATE)
Notes on Fuel Condition (e.g., cleanliness, odor) (TEXT)
System Shutdown & Return to Utility Power (STEP)
Time Utility Power Restored (DATE)
Voltage Level (Utility Power) (NUMBER)
Transfer Method to Utility Power (SELECTION options: Automatic, Manual, Both)
Observations During Return to Utility Power (e.g., voltage fluctuations, equipment behavior) (TEXT)
System Stability Upon Return (SELECTION options: Stable, Minor Fluctuations, Significant Fluctuations, Unstable)
Date of Return to Utility Power (DATE)
Any deviations from standard procedure during return to utility power? If so, describe. (TEXT)
Engineer Signature Verifying Return to Utility Power (SIGNATURE)
Post-Test Documentation & Reporting (STEP)
Date of Test (DATE)
Start Time of Test (DATE)
End Time of Test (DATE)
Generator Load Acceptance (kW) (NUMBER)
Transfer Time (Seconds) (NUMBER)
Transfer Success? (SELECTION options: Yes, No)
Observations & Deviations (TEXT)
Equipment Functionality Verified (Select All That Apply) (SELECTION options: Ventilators, Patient Monitors, Infusion Pumps, ECG Machines, Lighting, HVAC)
Generator Data Log (UPLOAD)
Technician Signature (SIGNATURE)